## I & O
Rapport 2025-1, Deposits, bilaga 1
Inputs | [5 empty] | Results
Term | Symbol | Unit | Value |  |  | Term | Symbol | Unit | AISI 304 | Sanicro 38 | AISI 304 max | Sanicro 38 max
Furnace height from the primary air port to nose arch upper edge | lh | (m) | 37.9 |  |  | Floor loading | HHRRt | (MW/m2) | 3.5929
Furnace width | lw | (m) | 13.526 |  |  | Heat flux average | qa | (kW/m2) | 106.8238
Furnace depth | ld | (m) | 15.028 |  |  | Heat flux | qt | (kW/m2) | 169.8568 |  | 170.918
Steam drum pressure | P | (bar) | 120 |  |  | Heat flux multiplier | kt | (%) | 159% |  | 160%
Higher heating value | HHVi | (MJ/kgDS) | 12.62 | or | Hardwood 13 (MJ/(kgDS)) | Temperature water/steam | Tw | (oC) | 324.68
Boiler load / DS firing rate | ṁDS | (tDS/day) | 5000 |  |  | Temperature deposit surface facing water | Twd | (oC) | 337.5584 |  | 337.6389
Tube outside diameter | Dtoi | (mm) | 63.5 |  |  | Temperature deposit-carbon steel interface | Tdc | (oC) | 394.1773 |  | 394.6115
Total wall thickness | xti | (mm) | 6.53 |  |  | Temperature carbon steel-cladding interface | Tcc | (oC) | 412.9198 | 412.9198 | 413.4746 | 413.4746
Cladding thickness 304 | xcli | (mm) | 1.65 |  |  | Temperature cladding surface facing furnace | Tcf | (oC) | 425.87 | 428.8094 | 426.5001 | 429.4548
Cladding thickness Sanicro 38 | xcli | (mm) | 1.65 |  |  | Corrosion rate | CR | (mm/y ) | 0.47653 | 0.04998 | 0.48212 | 0.051044
Thermal conductivity deposits | kdi | (W/mK) | 0.3 | or | Iron and other impurities (0,3 W/mK)
Average deposit thickness | xdi | (μm) | 100
Height observed from primary air port | li | (m) | 1.89

## I & O Exp
Inputs | [5 empty] | Results
Term | Symbol | Unit | Value |  |  | Term | Symbol | Unit | AISI 304 | Sanicro 38 | AISI 304 max | Sanicro 38 max
Furnace height from the primary air port to nose arch upper edge | lh | (m) | 37.9 |  |  | Boiler load / DS firing rate | ṁDS | (tDS/day) | 5000
Furnace width | lw | (m) | 13.526 |  |  | Heat input | Qt | (MW) | 730.3241
Furnace depth | ld | (m) | 15.028 |  |  | Floor area | Af | (m2) | 203.2687
Steam drum pressure | P | (bar) | 120 |  |  | Floor loading | HHRRt | (MW/m2) | 3.5929
Higher heating value | HHVi | (MJ/kgDS) | 12.62 | or | Hardwood 13 (MJ/(kgDS)) | Heat flux average | qa | (kW/m2) | 106.8238
Boiler load / DS firing rate | ṁDS | (tDS/day) | 5000 |  |  | Heat flux | qt | (kW/m2) | 169.8568 |  | 170.918
Tube outside diameter | Dtoi | (mm) | 63.5 |  |  | Heat flux multiplier | kt | (%) | 159% |  | 160%
Total wall thickness | xti | (mm) | 6.53 |  |  | Relative location percentage | l%i | (%) | 4.987%
Cladding thickness 304 | xcli | (mm) | 1.65 |  |  | Thermal conductivity water/steam | kw | (W/mK) | 0.51167
Cladding thickness Sanicro 38 | xcli | (mm) | 1.65 |  |  | Thermal conductivity deposits | kdt | (W/mK) | 0.3
Thermal conductivity deposits | kdi | (W/mK) | 0.3 | or | Iron and other impurities (0,3 W/mK) | Thermal conductivity carbon steel | kcst | (W/mK) | 44.2259 |  | 44.2176
Average deposit thickness | xdi | (μm) | 100 |  |  | Thermal conductivity cladding | kclt | (W/mK) | 21.6417 | 17.6382 | 21.651 | 17.6478
Height observed from primary air port | li | (m) | 1.89 | or |  | Thermal conductivity smelt | kss | (W/mK) | 0.6
[6 empty] | Average deposit thickness | xdi | (μm) | 100
Optional inputs | [5 empty] | Carbon steel thickness | xcst | (mm) | 4.88 | 4.88 | 4.88 | 4.88
Heat input | Qi | (MW) |  |  |  | Cladding thickness | xcli | (mm) | 1.65 | 1.65 | 1.65 | 1.65
Floor loading | HHRRi | (MW/m2) |  |  |  | Maximum smelt thickness | xs | (mm) | 1.039 | 1.0286 | 1.0303 | 1.0199
Heat flux | qi | (kW/m2) |  |  |  | Total wall thickness | xti | (mm) | 6.53
Thermal conductivity carbon steel | kcsi | (W/mK) |  |  |  | Tube outside diameter | Dtoi | (mm) | 63.5
Thermal conductivity cladding | kcli | (W/mK) |  |  |  | Tube inside diameter | Dti | (mm) | 50.44
Thermal conductivity cladding | kcli | (W/mK) |  |  |  | Tube inside area | Ati | (m2) | 0.0019982
Drum water velocity | uli | (m/s) |  |  |  | Water vapor-% | v-%t | (%) | 0%
Water vapor-% | v-%i | (%) |  |  |  | Water liquid-% | l-%t | (%) | 100%
Efficiency | ηi |  |  |  |  | Velocity water/steam | uw | (m/s) | 2
[6 empty] | Reynolds number | Re |  | 863834.3602
[6 empty] | Prandtl number | Pr |  | 1.0182
[6 empty] | Nusselt number | Nu |  | 1300.1882
[6 empty] | Heat transfer coefficient | h | (W/m2K) | 13189.28
[6 empty] | Temperature water/steam | Tw | (oC) | 324.68
[6 empty] | Temperature deposit surface facing water | Twd | (oC) | 337.5584 |  | 337.6389
[6 empty] | Temperature deposit-carbon steel interface | Tdc | (oC) | 394.1773 |  | 394.6115
[6 empty] | Temperature carbon steel-cladding interface | Tcc | (oC) | 412.9198 | 412.9198 | 413.4746 | 413.4746
[6 empty] | Temperature cladding surface facing furnace | Tcf | (oC) | 425.87 | 428.8094 | 426.5001 | 429.4548
[6 empty] | Temperature smelt surface facing furnace standard | Tss | (oC) | 720
[6 empty] | Corrosion rate | CR | (mm/y ) | 0.47653 | 0.04998 | 0.48212 | 0.051044

## Result screen
Term | Symbol | Unit | AISI 304 | Sanicro 38 | AISI 304 max | Sanicro 38 max
Furnace width | lw | (m) | 13.526
Furnace depth | ld | (m) | 15.028
Floor area | Af | (m2) | 203.2687
Boiler load / DS firing rate | ṁDS | (tDS/day) | 5000
Higher heating value | HHVt | (MJ/kgDS) | 12.62
Heat input | Qt | (MW) | 730.3241
Floor loading | HHRRt | (MW/m2) | 3.5929
Height observed from primary air port | li | (m) | 1.89
Furnace height from the primary air port to nose arch upper edge | lh | (m) | 37.9
Relative location percentage | l%i | (%) | 4.987%
Heat flux average | qa | (kW/m2) | 106.8238
Heat flux multiplier | kt | (%) | 159% |  | 160%
Heat flux | qt | (kW/m2) | 169.8568 |  | 170.918
Total wall thickness | xti | (mm) | 6.53
Tube outside diameter | Dtoi | (mm) | 63.5
Tube inside diameter | Dti | (mm) | 50.44
Tube inside area | Ati | (m2) | 0.0019982
Steam drum pressure | P | (bar) | 120
Drum water velocity | ult | (m/s) | 2
Density water liquid 100% | ρl | (kg/m3) | 655.18
Mass flow water liquid 100% | ṁl | (kg/s) | 2.6184
Water vapor-% | v-%t | (%) | 0%
Water liquid-% | l-%t | (%) | 100%
Velocity water/steam | uw | (m/s) | 2
Density water/steam | ρw | (kg/m3) | 655.18
Dynamic viscosity water/steam | μw | (Pa·s) | 7.6513e-05
Specific heat capacity water/steam | cw | (J/kgK) | 6809.1
Thermal conductivity water/steam | kw | (W/mK) | 0.51167
Reynolds number | Re |  | 863834.3602
Prandtl number | Pr |  | 1.0182
Nusselt number | Nu |  | 1300.1882
Heat transfer coefficient | h | (W/m2K) | 13189.28
Thermal conductivity deposits | kdt | (W/mK) | 0.3
Thermal conductivity carbon steel | kcst | (W/mK) | 44.2259 |  | 44.2176
Thermal conductivity cladding | kclt | (W/mK) | 21.6417 | 17.6382 | 21.651 | 17.6478
Thermal conductivity smelt | kss | (W/mK) | 0.6
Average deposit thickness | xdi | (μm) | 100
Carbon steel thickness | xcst | (mm) | 4.88 | 4.88 | 4.88 | 4.88
Cladding thickness | xcli | (mm) | 1.65 | 1.65 | 1.65 | 1.65
Maximum smelt thickness | xs | (mm) | 1.039 | 1.0286 | 1.0303 | 1.0199
Temperature water/steam | Tw | (oC) | 324.68
Temperature deposit surface facing water | Twd | (oC) | 337.5584 |  | 337.6389
Temperature deposit-carbon steel interface | Tdc | (oC) | 394.1773 |  | 394.6115
Temperature carbon steel-cladding interface | Tcc | (oC) | 412.9198 | 412.9198 | 413.4746 | 413.4746
Temperature cladding surface facing furnace | Tcf | (oC) | 425.87 | 428.8094 | 426.5001 | 429.4548
Temperature smelt surface facing furnace | Tss | (oC) | 720
Corrosion rate | CR | (mm/y ) | 0.47653 | 0.04998 | 0.48212 | 0.051044

## CM
Term | Symbol | Unit | AISI 304 | Sanicro 38 | AISI 304 max | Sanicro 38 max
Boiler load / DS firing rate | ṁDS | (tDS/day) | 5000
Boiler load / DS firing rate | ṁDS | (kgDS/s) | 57.8704
Higher heating value choice | HHVc | (MJ/kgDS) | Hardwood 13 (MJ/(kgDS))
Higher heating value choice | HHVc | (MJ/kgDS) | 13
Higher heating value input | HHVi | (MJ/kgDS) | 12.62
Higher heating value true | HHVt | (MJ/kgDS) | 12.62
Heat input calculated | Qc | (MW) | 730.3241
Heat input input | Qi | (MW) | 0
Heat input true | Qt | (MW) | 730.3241
Furnace width | lw | (m) | 13.526
Furnace depth | ld | (m) | 15.028
Floor area | Af | (m2) | 203.2687
Floor loading calculated | HHRRc | (MW/m2) | 3.5929
Floor loading input | HHRRi | (MW/m2) | 0
Floor loading true | HHRRt | (MW/m2) | 3.5929
Equation parameter heat flux a | aq |  | 30.5147 |  | 48.8235
Equation parameter heat flux b | bq |  | -2.8125 |  | -4.5
Heat flux function | qf | (W/m2) | 106823.7664 |  | 170918.024
Efficiency standard | ηs |  | 100%
Efficiency input | ηi |  | 0%
Efficiency true | ηt |  | 100%
Heat flux efficiency | qe | (W/m2) | 106823.7664 |  | 170918.024
Height observed from primary air port choice | lc | (%) | 0
Relative location percentage choice | l%c | (%) | No Match
Heat flux multiplier choice | kc | (%) | Out of Range
Height observed from primary air port input | li | (m) | 1.89
Furnace height from the primary air port to nose arch upper edge | lh | (m) | 37.9
Relative location percentage input | l%i | (%) | 4.987%
Heat flux multiplier input | ki | (%) | 159% |  | 160%
Heat flux multiplier true | kt | (%) | 159% |  | 160%
Heat flux calculated | qc | (W/m2) | 169856.8349 |  | 170918.0262
Heat flux input | qi | (kW/m2) | 0
Heat flux input conversion | qi | (W/m2) | 0
Heat flux true | qt | (W/m2) | 169856.8349 |  | 170918.0262
Heat flux average conversion | qa | (kW/m2) | 106.8238
Heat flux true conversion | qt | (kW/m2) | 169.8568 |  | 170.918
Tube outside diameter input | Dtoi | (mm) | 63.5
Tube outside diameter input conversion | Dtoi | (m) | 0.0635
Tube outside diameter standard | Dtos | (m) | 0.0635
Tube outside diameter true | Dtot | (m) | 0.0635
Total wall thickness input | xti | (mm) | 6.53
Total wall thickness input conversion | xti | (m) | 0.00653
Total wall thickness standard | xts | (m) | 0.00653
Total wall thickness true | xtt | (m) | 0.00653
Cladding thickness input | xcli | (mm) | 1.65 | 1.65 | 1.65 | 1.65
Cladding thickness input conversion | xcli | (m) | 0.00165 | 0.00165 | 0.00165 | 0.00165
Cladding thickness standard | xcls | (m) | 0.00165 | 0.00182 | 0.00165 | 0.00182
Cladding thickness true | xclt | (m) | 0.00165 | 0.00165 | 0.00165 | 0.00165
Carbon steel thickness true | xcst | (m) | 0.00488 | 0.00488 | 0.00488 | 0.00488
Carbon steel thickness conversion | xcst | (mm) | 4.88 | 4.88 | 4.88 | 4.88
Tube inside diameter | Dti | (m) | 0.05044
Tube inside area | Ati | (m2) | 0.0019982
Drum water velocity input | uli | (m/s) | 0
Drum water velocity standard | uls | (m/s) | 2
Drum water velocity true | ult | (m/s) | 2
Water vapor-% input | v-%i | (%) | 0%
Water vapor-% standard | v-%s | (%) | 0%
Water vapor-% true | v-%t | (%) | 0%
Water liquid-% true | l-%t | (%) | 100%
Steam drum pressure | P | (bar) | 120
Density water/steam | ρw | (kg/m3) | 655.18
Dynamic viscosity water/steam | μw | (Pa·s) | 7.6513e-05
Specific heat capacity water/steam | cw | (J/kgK) | 6809.1
Thermal conductivity water/steam | kw | (W/mK) | 0.51167
Temperature water/steam | Tw | (oC) | 324.68
Density water liquid 100% | ρl | (kg/m3) | 655.18
Mass flow water liquid 100% | ṁl | (kg/s) | 2.6184
Velocity water/steam | uw | (m/s) | 2
Reynolds number | Re |  | 863834.3602
Prandtl number | Pr |  | 1.0182
Nusselt number | Nu |  | 1300.1882
Heat transfer coefficient | h | (W/m2K) | 13189.28
Temperature deposit surface facing water | Twd | (oC) | 337.5584 |  | 337.6389
Thermal conductivity deposits choice | kdc | (W/mK) | Iron and other impurities (0,3 W/mK)
Thermal conductivity deposits choice | kdc | (W/mK) | 0.3
Thermal conductivity deposits input | kdi | (W/mK) | 0.3
Thermal conductivity deposits true | kdt | (W/mK) | 0.3
Average deposit thickness input | xdi | (μm) | 100
Average deposit thickness true | xdt | (m) | 0.0001
Temperature deposit-carbon steel interface | Tdc | (oC) | 394.1773 |  | 394.6115
Equation parameter k carbon steel a | acs |  | -2.1429e-05
Equation parameter k carbon steel b | bcs |  | -0.0021429
Equation parameter k carbon steel c | ccs |  | 48.4
Thermal conductivity carbon steel function | kcsf | (W/mK) | 44.2259 |  | 44.2176
Thermal conductivity carbon steel input | kcsi | (W/mK) | 0
Thermal conductivity carbon steel true | kcst | (W/mK) | 44.2259 |  | 44.2176
Temperature carbon steel-cladding interface | Tcc | (oC) | 412.9198 | 412.9198 | 413.4746 | 413.4746
Equation parameter k cladding a | acl |  | 0.016827 | 0.017227 | 0.016827 | 0.017227
Equation parameter k cladding b | bcl |  | 14.6936 | 10.5249 | 14.6936 | 10.5249
Thermal conductivity cladding function | kclf | (W/mK) | 21.6417 | 17.6382 | 21.651 | 17.6478
Thermal conductivity cladding input | kcli | (W/mK) | 0 | 0 | 0 | 0
Thermal conductivity cladding true | kclt | (W/mK) | 21.6417 | 17.6382 | 21.651 | 17.6478
Temperature cladding surface facing furnace | Tcf | (oC) | 425.87 | 428.8094 | 426.5001 | 429.4548
Thermal conductivity smelt standard | kss | (W/mK) | 0.6
Temperature smelt surface facing furnace standard | Tss | (oC) | 720
Maximum smelt thickness | xs | (mm) | 1.039 | 1.0286 | 1.0303 | 1.0199
Equation parameter CR a | aCR |  | -9.7292e-06 | 1.3254e-05 | -9.7292e-06 | 1.3254e-05
Equation parameter CR b | bCR |  | 0.017162 | -0.0097262 | 0.017162 | -0.0097262
Equation parameter CR c | cCR |  | -5.0678 | 1.7836 | -5.0678 | 1.7836
Temperature 0 CR | TnCR | (oC) | 375.0137 | 374.6512 | 375.0137 | 374.6512
Corrosion rate | CR | (mm/y ) | 0.47653 | 0.04998 | 0.48212 | 0.051044

## q-Q
Wood type | Higher heating value | Floor loading (HHRR) | Heat flux max (qm) | Heat flux average (qa) |  |  | Average heat flux | Maximum heat flux
| (MJ/(kgDS)) | (MW/m2) | (kW/m2) | (kW/m2) | Equation parameter heat flux a | aq | 30.5147 | 48.8235
|  | 3 | 140 | 87.5 | Equation parameter heat flux b | bq | -2.8125 | -4.5
Softwood 14 (MJ/(kgDS)) | 14 | 3.3 | 160 | 100
Hardwood 13 (MJ/(kgDS)) | 13 | 3.5 | 166 | 103.75
|  | 3.8 | 180 | 112.5
Hardwood 13 (MJ/(kgDS)) | 13

## l-v table
| Both |  | Liquid | [12 empty] | Vapor
| P | Tw | ρw | μw | cw | kw | Volume | Internal Energy | Enthalpy | Entropy | Cv | Sound Spd | Joule-Thomson | Surf, Tension |  | Pressure | Temperature | ρw | μw | cw | kw | Volume | Internal Energy | Enthalpy | Entropy | Cv | Sound Spd | Joule-Thomson | Internal Energy (kJ/kg) | Enthalpy (kJ/kg) | Entropy (J/g*K) | Cv (J/g*K) | Cp (J/g*K) | Internal Energy (kJ/kg) | Enthalpy (kJ/kg) | Entropy (J/g*K) | Cv (J/g*K) | Cp (J/g*K)
| (bar) | (oC) | (kg/m3) | (Pa·s) | (J/kgK) | (W/mK) | (m3/kg) | (J/kg) | (J/kg) | (J/kgK) | (J/kgK) | (m/s) | (K/bar) | (N/m) |  | (bar) | (oC) | (kg/m3) | (Pa·s) | (J/kgK) | (W/mK) | (m3/kg) | (J/kg) | (J/kg) | (J/kgK) | (J/kgK) | (m/s) | (K/bar)
| 60 | 275.58 | 758 | 9.5311e-05 | 5211.6 | 0.58679 | 0.0013193 | 1206000 | 1213900 | 3027.8 | 3093.9 | 1033.9 | 0.0089409 | 0.020026 |  | 60 | 275.58 | 30.818 | 1.844e-05 | 4879.4 | 0.059066 | 0.032448 | 2589900 | 2784600 | 5890.1 | 2705.4 | 493.84 | 1.3102 | 1206 | 1213.9 | 3.0278 | 3.0939 | 5.2116 | 2589.9 | 2784.6 | 5.8901 | 2.7054 | 4.8794
| 61 | 276.67 | 756.13 | 9.4877e-05 | 5229.9 | 0.5854 | 0.0013225 | 1211400 | 1219500 | 3037.7 | 3091.7 | 1028.7 | 0.0093774 | 0.019773 |  | 61 | 276.67 | 31.378 | 1.8486e-05 | 4925.3 | 0.059499 | 0.03187 | 2589100 | 2783500 | 5882.3 | 2716.3 | 493.39 | 1.2992 | 1211.4 | 1219.5 | 3.0377 | 3.0917 | 5.2299 | 2589.1 | 2783.5 | 5.8823 | 2.7163 | 4.9253
| 62 | 277.73 | 754.27 | 9.4451e-05 | 5248.4 | 0.58401 | 0.0013258 | 1216800 | 1225100 | 3047.6 | 3089.5 | 1023.6 | 0.0098169 | 0.019523 |  | 62 | 277.73 | 31.94 | 1.8531e-05 | 4971.5 | 0.059933 | 0.031309 | 2588300 | 2782400 | 5874.5 | 2727.1 | 492.93 | 1.2884 | 1216.8 | 1225.1 | 3.0476 | 3.0895 | 5.2484 | 2588.3 | 2782.4 | 5.8745 | 2.7271 | 4.9715
| 63 | 278.79 | 752.42 | 9.4031e-05 | 5267 | 0.58263 | 0.001329 | 1222200 | 1230500 | 3057.3 | 3087.3 | 1018.5 | 0.01026 | 0.019277 |  | 63 | 278.79 | 32.504 | 1.8577e-05 | 5018.2 | 0.060368 | 0.030766 | 2587400 | 2781200 | 5866.8 | 2737.8 | 492.47 | 1.2778 | 1222.2 | 1230.5 | 3.0573 | 3.0873 | 5.267 | 2587.4 | 2781.2 | 5.8668 | 2.7378 | 5.0182
| 64 | 279.83 | 750.58 | 9.3618e-05 | 5285.8 | 0.58125 | 0.0013323 | 1227500 | 1236000 | 3066.9 | 3085.3 | 1013.4 | 0.010705 | 0.019033 |  | 64 | 279.83 | 33.07 | 1.8622e-05 | 5065.3 | 0.060805 | 0.030238 | 2586500 | 2780100 | 5859.2 | 2748.5 | 492 | 1.2674 | 1227.5 | 1236 | 3.0669 | 3.0853 | 5.2858 | 2586.5 | 2780.1 | 5.8592 | 2.7485 | 5.0653
| 65 | 280.86 | 748.75 | 9.3211e-05 | 5304.8 | 0.57989 | 0.0013356 | 1232700 | 1241400 | 3076.4 | 3083.2 | 1008.4 | 0.011154 | 0.018792 |  | 65 | 280.86 | 33.64 | 1.8667e-05 | 5112.7 | 0.061243 | 0.029727 | 2585700 | 2778900 | 5851.6 | 2759.2 | 491.53 | 1.2572 | 1232.7 | 1241.4 | 3.0764 | 3.0832 | 5.3048 | 2585.7 | 2778.9 | 5.8516 | 2.7592 | 5.1127
| 66 | 281.87 | 746.93 | 9.2811e-05 | 5323.9 | 0.57853 | 0.0013388 | 1237900 | 1246700 | 3085.8 | 3081.3 | 1003.4 | 0.011606 | 0.018555 |  | 66 | 281.87 | 34.211 | 1.8712e-05 | 5160.6 | 0.061682 | 0.02923 | 2584700 | 2777700 | 5844.1 | 2769.8 | 491.06 | 1.2473 | 1237.9 | 1246.7 | 3.0858 | 3.0813 | 5.3239 | 2584.7 | 2777.7 | 5.8441 | 2.7698 | 5.1606
| 67 | 282.88 | 745.11 | 9.2416e-05 | 5343.3 | 0.57717 | 0.0013421 | 1243000 | 1252000 | 3095.1 | 3079.4 | 998.43 | 0.012062 | 0.01832 |  | 67 | 282.88 | 34.786 | 1.8756e-05 | 5208.9 | 0.062123 | 0.028747 | 2583800 | 2776400 | 5836.7 | 2780.3 | 490.58 | 1.2375 | 1243 | 1252 | 3.0951 | 3.0794 | 5.3433 | 2583.8 | 2776.4 | 5.8367 | 2.7803 | 5.2089
| 68 | 283.87 | 743.31 | 9.2027e-05 | 5362.8 | 0.57583 | 0.0013453 | 1248100 | 1257300 | 3104.3 | 3077.5 | 993.49 | 0.012521 | 0.018089 |  | 68 | 283.87 | 35.363 | 1.8801e-05 | 5257.7 | 0.062566 | 0.028278 | 2582900 | 2775200 | 5829.3 | 2790.7 | 490.09 | 1.2279 | 1248.1 | 1257.3 | 3.1043 | 3.0775 | 5.3628 | 2582.9 | 2775.2 | 5.8293 | 2.7907 | 5.2577
| 69 | 284.86 | 741.51 | 9.1644e-05 | 5382.5 | 0.57448 | 0.0013486 | 1253200 | 1262500 | 3113.4 | 3075.7 | 988.58 | 0.012984 | 0.01786 |  | 69 | 284.86 | 35.943 | 1.8845e-05 | 5306.9 | 0.063011 | 0.027822 | 2581900 | 2773900 | 5822 | 2801.2 | 489.6 | 1.2185 | 1253.2 | 1262.5 | 3.1134 | 3.0757 | 5.3825 | 2581.9 | 2773.9 | 5.822 | 2.8012 | 5.3069
| 70 | 285.83 | 739.72 | 9.1266e-05 | 5402.5 | 0.57315 | 0.0013519 | 1258200 | 1267700 | 3122.4 | 3074 | 983.7 | 0.01345 | 0.017633 |  | 70 | 285.83 | 36.525 | 1.8889e-05 | 5356.6 | 0.063457 | 0.027378 | 2581000 | 2772600 | 5814.8 | 2811.5 | 489.11 | 1.2093 | 1258.2 | 1267.7 | 3.1224 | 3.074 | 5.4025 | 2581 | 2772.6 | 5.8148 | 2.8115 | 5.3566
| 71 | 286.79 | 737.94 | 9.0894e-05 | 5422.6 | 0.57182 | 0.0013551 | 1263200 | 1272800 | 3131.3 | 3072.3 | 978.84 | 0.01392 | 0.01741 |  | 71 | 286.79 | 37.11 | 1.8933e-05 | 5406.8 | 0.063906 | 0.026947 | 2580000 | 2771300 | 5807.6 | 2821.9 | 488.61 | 1.2002 | 1263.2 | 1272.8 | 3.1313 | 3.0723 | 5.4226 | 2580 | 2771.3 | 5.8076 | 2.8219 | 5.4068
| 72 | 287.74 | 736.17 | 9.0526e-05 | 5443 | 0.5705 | 0.0013584 | 1268100 | 1277900 | 3140.2 | 3070.7 | 974.01 | 0.014394 | 0.017189 |  | 72 | 287.74 | 37.698 | 1.8977e-05 | 5457.4 | 0.064357 | 0.026526 | 2579000 | 2770000 | 5800.4 | 2832.1 | 488.11 | 1.1914 | 1268.1 | 1277.9 | 3.1402 | 3.0707 | 5.443 | 2579 | 2770 | 5.8004 | 2.8321 | 5.4574
| 73 | 288.68 | 734.4 | 9.0163e-05 | 5463.5 | 0.56918 | 0.0013617 | 1273000 | 1282900 | 3148.9 | 3069.1 | 969.21 | 0.014871 | 0.01697 |  | 73 | 288.68 | 38.289 | 1.9021e-05 | 5508.6 | 0.06481 | 0.026117 | 2578000 | 2768600 | 5793.3 | 2842.4 | 487.6 | 1.1826 | 1273 | 1282.9 | 3.1489 | 3.0691 | 5.4635 | 2578 | 2768.6 | 5.7933 | 2.8424 | 5.5086
| 74 | 289.61 | 732.64 | 8.9805e-05 | 5484.3 | 0.56786 | 0.0013649 | 1277800 | 1287900 | 3157.6 | 3067.6 | 964.43 | 0.015353 | 0.016754 |  | 74 | 289.61 | 38.883 | 1.9065e-05 | 5560.3 | 0.065265 | 0.025718 | 2577000 | 2767300 | 5786.3 | 2852.5 | 487.09 | 1.174 | 1277.8 | 1287.9 | 3.1576 | 3.0676 | 5.4843 | 2577 | 2767.3 | 5.7863 | 2.8525 | 5.5603
| 75 | 290.54 | 730.88 | 8.9451e-05 | 5505.4 | 0.56656 | 0.0013682 | 1282700 | 1292900 | 3166.2 | 3066.1 | 959.68 | 0.015838 | 0.01654 |  | 75 | 290.54 | 39.479 | 1.9109e-05 | 5612.5 | 0.065723 | 0.02533 | 2575900 | 2765900 | 5779.3 | 2862.7 | 486.58 | 1.1656 | 1282.7 | 1292.9 | 3.1662 | 3.0661 | 5.5054 | 2575.9 | 2765.9 | 5.7793 | 2.8627 | 5.6125
| 76 | 291.45 | 729.14 | 8.9102e-05 | 5526.6 | 0.56525 | 0.0013715 | 1287400 | 1297900 | 3174.7 | 3064.6 | 954.95 | 0.016328 | 0.016329 |  | 76 | 291.45 | 40.079 | 1.9152e-05 | 5665.3 | 0.066184 | 0.024951 | 2574900 | 2764500 | 5772.3 | 2872.8 | 486.06 | 1.1573 | 1287.4 | 1297.9 | 3.1747 | 3.0646 | 5.5266 | 2574.9 | 2764.5 | 5.7723 | 2.8728 | 5.6653
| 77 | 292.35 | 727.39 | 8.8756e-05 | 5548.1 | 0.56396 | 0.0013748 | 1292200 | 1302800 | 3183.2 | 3063.3 | 950.24 | 0.016821 | 0.01612 |  | 77 | 292.35 | 40.681 | 1.9196e-05 | 5718.7 | 0.066647 | 0.024581 | 2573800 | 2763100 | 5765.4 | 2882.9 | 485.54 | 1.1492 | 1292.2 | 1302.8 | 3.1832 | 3.0633 | 5.5481 | 2573.8 | 2763.1 | 5.7654 | 2.8829 | 5.7187
| 78 | 293.25 | 725.66 | 8.8415e-05 | 5569.8 | 0.56267 | 0.0013781 | 1296900 | 1307700 | 3191.5 | 3061.9 | 945.56 | 0.01732 | 0.015913 |  | 78 | 293.25 | 41.287 | 1.9239e-05 | 5772.6 | 0.067113 | 0.024221 | 2572700 | 2761600 | 5758.6 | 2892.9 | 485.01 | 1.1411 | 1296.9 | 1307.7 | 3.1915 | 3.0619 | 5.5698 | 2572.7 | 2761.6 | 5.7586 | 2.8929 | 5.7726
| 79 | 294.13 | 723.92 | 8.8078e-05 | 5591.8 | 0.56138 | 0.0013814 | 1301600 | 1312500 | 3199.8 | 3060.6 | 940.9 | 0.017822 | 0.015709 |  | 79 | 294.13 | 41.895 | 1.9282e-05 | 5827.1 | 0.067583 | 0.023869 | 2571600 | 2760200 | 5751.8 | 2902.9 | 484.48 | 1.1332 | 1301.6 | 1312.5 | 3.1998 | 3.0606 | 5.5918 | 2571.6 | 2760.2 | 5.7518 | 2.9029 | 5.8271
| 80 | 295.01 | 722.2 | 8.7745e-05 | 5614.1 | 0.5601 | 0.0013847 | 1306200 | 1317300 | 3208.1 | 3059.4 | 936.26 | 0.018329 | 0.015507 |  | 80 | 295.01 | 42.507 | 1.9326e-05 | 5882.3 | 0.068055 | 0.023526 | 2570500 | 2758700 | 5745 | 2912.8 | 483.94 | 1.1255 | 1306.2 | 1317.3 | 3.2081 | 3.0594 | 5.6141 | 2570.5 | 2758.7 | 5.745 | 2.9128 | 5.8823
| 81 | 295.88 | 720.47 | 8.7415e-05 | 5636.6 | 0.55882 | 0.001388 | 1310900 | 1322100 | 3216.2 | 3058.2 | 931.64 | 0.01884 | 0.015307 |  | 81 | 295.88 | 43.122 | 1.9369e-05 | 5938.1 | 0.06853 | 0.02319 | 2569300 | 2757200 | 5738.3 | 2922.8 | 483.41 | 1.1178 | 1310.9 | 1322.1 | 3.2162 | 3.0582 | 5.6366 | 2569.3 | 2757.2 | 5.7383 | 2.9228 | 5.9381
| 82 | 296.74 | 718.76 | 8.7089e-05 | 5659.4 | 0.55754 | 0.0013913 | 1315400 | 1326800 | 3224.3 | 3057 | 927.04 | 0.019356 | 0.015109 |  | 82 | 296.74 | 43.74 | 1.9412e-05 | 5994.5 | 0.069009 | 0.022863 | 2568200 | 2755700 | 5731.6 | 2932.7 | 482.86 | 1.1103 | 1315.4 | 1326.8 | 3.2243 | 3.057 | 5.6594 | 2568.2 | 2755.7 | 5.7316 | 2.9327 | 5.9945
| 83 | 297.59 | 717.04 | 8.6766e-05 | 5682.4 | 0.55628 | 0.0013946 | 1320000 | 1331600 | 3232.4 | 3055.9 | 922.47 | 0.019877 | 0.014913 |  | 83 | 297.59 | 44.361 | 1.9455e-05 | 6051.5 | 0.069491 | 0.022542 | 2567000 | 2754100 | 5724.9 | 2942.5 | 482.32 | 1.1029 | 1320 | 1331.6 | 3.2324 | 3.0559 | 5.6824 | 2567 | 2754.1 | 5.7249 | 2.9425 | 6.0515
| 84 | 298.43 | 715.34 | 8.6447e-05 | 5705.8 | 0.55501 | 0.0013979 | 1324500 | 1336300 | 3240.3 | 3054.9 | 917.91 | 0.020402 | 0.014719 |  | 84 | 298.43 | 44.985 | 1.9499e-05 | 6109.3 | 0.069977 | 0.022229 | 2565900 | 2752600 | 5718.3 | 2952.4 | 481.77 | 1.0956 | 1324.5 | 1336.3 | 3.2403 | 3.0549 | 5.7058 | 2565.9 | 2752.6 | 5.7183 | 2.9524 | 6.1093
| 85 | 299.27 | 713.63 | 8.6131e-05 | 5729.4 | 0.55375 | 0.0014013 | 1329000 | 1340900 | 3248.3 | 3053.9 | 913.37 | 0.020932 | 0.014527 |  | 85 | 299.27 | 45.613 | 1.9542e-05 | 6167.7 | 0.070466 | 0.021923 | 2564700 | 2751000 | 5711.7 | 2962.2 | 481.22 | 1.0884 | 1329 | 1340.9 | 3.2483 | 3.0539 | 5.7294 | 2564.7 | 2751 | 5.7117 | 2.9622 | 6.1677
| 86 | 300.1 | 711.93 | 8.5818e-05 | 5753.3 | 0.55249 | 0.0014046 | 1333500 | 1345600 | 3256.1 | 3052.9 | 908.86 | 0.021468 | 0.014337 |  | 86 | 300.1 | 46.244 | 1.9585e-05 | 6226.9 | 0.07096 | 0.021624 | 2563500 | 2749400 | 5705.1 | 2971.9 | 480.66 | 1.0813 | 1333.5 | 1345.6 | 3.2561 | 3.0529 | 5.7533 | 2563.5 | 2749.4 | 5.7051 | 2.9719 | 6.2269
| 87 | 300.92 | 710.23 | 8.5508e-05 | 5777.5 | 0.55124 | 0.001408 | 1337900 | 1350200 | 3263.9 | 3052 | 904.36 | 0.022008 | 0.014149 |  | 87 | 300.92 | 46.879 | 1.9628e-05 | 6286.8 | 0.071457 | 0.021332 | 2562300 | 2747800 | 5698.6 | 2981.7 | 480.1 | 1.0743 | 1337.9 | 1350.2 | 3.2639 | 3.052 | 5.7775 | 2562.3 | 2747.8 | 5.6986 | 2.9817 | 6.2868
| 88 | 301.74 | 708.54 | 8.5201e-05 | 5802.1 | 0.54999 | 0.0014114 | 1342300 | 1354800 | 3271.7 | 3051.1 | 899.87 | 0.022553 | 0.013963 |  | 88 | 301.74 | 47.517 | 1.9671e-05 | 6347.4 | 0.071958 | 0.021045 | 2561000 | 2746200 | 5692.1 | 2991.4 | 479.54 | 1.0674 | 1342.3 | 1354.8 | 3.2717 | 3.0511 | 5.8021 | 2561 | 2746.2 | 5.6921 | 2.9914 | 6.3474
| 89 | 302.54 | 706.85 | 8.4897e-05 | 5826.9 | 0.54875 | 0.0014147 | 1346700 | 1359300 | 3279.3 | 3050.2 | 895.41 | 0.023104 | 0.013778 |  | 89 | 302.54 | 48.159 | 1.9715e-05 | 6408.8 | 0.072464 | 0.020765 | 2559800 | 2744600 | 5685.6 | 3001.1 | 478.97 | 1.0606 | 1346.7 | 1359.3 | 3.2793 | 3.0502 | 5.8269 | 2559.8 | 2744.6 | 5.6856 | 3.0011 | 6.4088
| 90 | 303.34 | 705.16 | 8.4595e-05 | 5852.1 | 0.54751 | 0.0014181 | 1351100 | 1363900 | 3287 | 3049.4 | 890.96 | 0.02366 | 0.013596 |  | 90 | 303.34 | 48.804 | 1.9758e-05 | 6471 | 0.072973 | 0.02049 | 2558500 | 2742900 | 5679.1 | 3010.8 | 478.4 | 1.0538 | 1351.1 | 1363.9 | 3.287 | 3.0494 | 5.8521 | 2558.5 | 2742.9 | 5.6791 | 3.0108 | 6.471
| 91 | 304.14 | 703.48 | 8.4297e-05 | 5877.6 | 0.54627 | 0.0014215 | 1355500 | 1368400 | 3294.6 | 3048.7 | 886.53 | 0.024222 | 0.013415 |  | 91 | 304.14 | 49.453 | 1.9801e-05 | 6534 | 0.073488 | 0.020221 | 2557300 | 2741300 | 5672.7 | 3020.4 | 477.83 | 1.0472 | 1355.5 | 1368.4 | 3.2946 | 3.0487 | 5.8776 | 2557.3 | 2741.3 | 5.6727 | 3.0204 | 6.534
| 92 | 304.93 | 701.8 | 8.4001e-05 | 5903.5 | 0.54504 | 0.0014249 | 1359800 | 1372900 | 3302.1 | 3048 | 882.11 | 0.024789 | 0.013236 |  | 92 | 304.93 | 50.105 | 1.9845e-05 | 6597.8 | 0.074007 | 0.019958 | 2556000 | 2739600 | 5666.3 | 3030.1 | 477.25 | 1.0407 | 1359.8 | 1372.9 | 3.3021 | 3.048 | 5.9035 | 2556 | 2739.6 | 5.6663 | 3.0301 | 6.5978
| 93 | 305.71 | 700.12 | 8.3707e-05 | 5929.7 | 0.54381 | 0.0014283 | 1364100 | 1377400 | 3309.6 | 3047.3 | 877.71 | 0.025362 | 0.013059 |  | 93 | 305.71 | 50.761 | 1.9888e-05 | 6662.5 | 0.074531 | 0.0197 | 2554700 | 2737900 | 5659.9 | 3039.7 | 476.67 | 1.0342 | 1364.1 | 1377.4 | 3.3096 | 3.0473 | 5.9297 | 2554.7 | 2737.9 | 5.6599 | 3.0397 | 6.6625
| 94 | 306.48 | 698.44 | 8.3416e-05 | 5956.2 | 0.54258 | 0.0014318 | 1368300 | 1381800 | 3317 | 3046.7 | 873.33 | 0.025941 | 0.012883 |  | 94 | 306.48 | 51.421 | 1.9932e-05 | 6728 | 0.075059 | 0.019447 | 2553400 | 2736200 | 5653.6 | 3049.3 | 476.08 | 1.0279 | 1368.3 | 1381.8 | 3.317 | 3.0467 | 5.9562 | 2553.4 | 2736.2 | 5.6536 | 3.0493 | 6.728
| 95 | 307.25 | 696.77 | 8.3128e-05 | 5983.2 | 0.54136 | 0.0014352 | 1372600 | 1386200 | 3324.4 | 3046.1 | 868.96 | 0.026525 | 0.012709 |  | 95 | 307.25 | 52.085 | 1.9975e-05 | 6794.5 | 0.075593 | 0.019199 | 2552000 | 2734400 | 5647.3 | 3058.9 | 475.5 | 1.0216 | 1372.6 | 1386.2 | 3.3244 | 3.0461 | 5.9832 | 2552 | 2734.4 | 5.6473 | 3.0589 | 6.7945
| 96 | 308.01 | 695.09 | 8.2842e-05 | 6010.5 | 0.54014 | 0.0014387 | 1376800 | 1390600 | 3331.7 | 3045.5 | 864.61 | 0.027116 | 0.012537 |  | 96 | 308.01 | 52.753 | 2.0019e-05 | 6861.8 | 0.076132 | 0.018956 | 2550700 | 2732700 | 5641 | 3068.4 | 474.91 | 1.0154 | 1376.8 | 1390.6 | 3.3317 | 3.0455 | 6.0105 | 2550.7 | 2732.7 | 5.641 | 3.0684 | 6.8618
| 97 | 308.77 | 693.42 | 8.2558e-05 | 6038.2 | 0.53892 | 0.0014421 | 1381000 | 1395000 | 3339 | 3045 | 860.27 | 0.027712 | 0.012367 |  | 97 | 308.77 | 53.424 | 2.0063e-05 | 6930.1 | 0.076677 | 0.018718 | 2549300 | 2730900 | 5634.7 | 3078 | 474.31 | 1.0092 | 1381 | 1395 | 3.339 | 3.045 | 6.0382 | 2549.3 | 2730.9 | 5.6347 | 3.078 | 6.9301
| 98 | 309.52 | 691.76 | 8.2276e-05 | 6066.3 | 0.53771 | 0.0014456 | 1385200 | 1399400 | 3346.3 | 3044.6 | 855.94 | 0.028315 | 0.012198 |  | 98 | 309.52 | 54.1 | 2.0106e-05 | 6999.3 | 0.077226 | 0.018484 | 2548000 | 2729100 | 5628.4 | 3087.5 | 473.71 | 1.0032 | 1385.2 | 1399.4 | 3.3463 | 3.0446 | 6.0663 | 2548 | 2729.1 | 5.6284 | 3.0875 | 6.9993
| 99 | 310.26 | 690.09 | 8.1996e-05 | 6094.8 | 0.5365 | 0.0014491 | 1389400 | 1403700 | 3353.5 | 3044.2 | 851.63 | 0.028924 | 0.01203 |  | 99 | 310.26 | 54.779 | 2.015e-05 | 7069.6 | 0.077782 | 0.018255 | 2546600 | 2727300 | 5622.2 | 3097 | 473.11 | 0.99716 | 1389.4 | 1403.7 | 3.3535 | 3.0442 | 6.0948 | 2546.6 | 2727.3 | 5.6222 | 3.097 | 7.0696
| 100 | 311 | 688.42 | 8.1718e-05 | 6123.7 | 0.53529 | 0.0014526 | 1393500 | 1408100 | 3360.6 | 3043.8 | 847.33 | 0.02954 | 0.011865 |  | 100 | 311 | 55.463 | 2.0194e-05 | 7140.8 | 0.078344 | 0.01803 | 2545200 | 2725500 | 5616 | 3106.5 | 472.51 | 0.99124 | 1393.5 | 1408.1 | 3.3606 | 3.0438 | 6.1237 | 2545.2 | 2725.5 | 5.616 | 3.1065 | 7.1408
| 101 | 311.73 | 686.76 | 8.1443e-05 | 6153 | 0.53409 | 0.0014561 | 1397700 | 1412400 | 3367.8 | 3043.5 | 843.04 | 0.030162 | 0.0117 |  | 101 | 311.73 | 56.151 | 2.0239e-05 | 7213.1 | 0.078911 | 0.017809 | 2543800 | 2723700 | 5609.7 | 3116 | 471.9 | 0.98538 | 1397.7 | 1412.4 | 3.3678 | 3.0435 | 6.153 | 2543.8 | 2723.7 | 5.6097 | 3.116 | 7.2131
| 102 | 312.46 | 685.1 | 8.1169e-05 | 6182.8 | 0.53289 | 0.0014596 | 1401800 | 1416700 | 3374.9 | 3043.2 | 838.77 | 0.030791 | 0.011538 |  | 102 | 312.46 | 56.843 | 2.0283e-05 | 7286.5 | 0.079485 | 0.017592 | 2542400 | 2721800 | 5603.5 | 3125.4 | 471.29 | 0.97959 | 1401.8 | 1416.7 | 3.3749 | 3.0432 | 6.1828 | 2542.4 | 2721.8 | 5.6035 | 3.1254 | 7.2865
| 103 | 313.18 | 683.43 | 8.0897e-05 | 6213.1 | 0.53169 | 0.0014632 | 1405900 | 1420900 | 3381.9 | 3042.9 | 834.51 | 0.031427 | 0.011376 |  | 103 | 313.18 | 57.54 | 2.0327e-05 | 7360.9 | 0.080065 | 0.017379 | 2540900 | 2719900 | 5597.4 | 3134.9 | 470.67 | 0.97387 | 1405.9 | 1420.9 | 3.3819 | 3.0429 | 6.2131 | 2540.9 | 2719.9 | 5.5974 | 3.1349 | 7.3609
| 104 | 313.89 | 681.77 | 8.0627e-05 | 6243.8 | 0.53049 | 0.0014668 | 1410000 | 1425200 | 3388.9 | 3042.7 | 830.26 | 0.03207 | 0.011217 |  | 104 | 313.89 | 58.24 | 2.0372e-05 | 7436.5 | 0.080652 | 0.01717 | 2539500 | 2718000 | 5591.2 | 3144.3 | 470.05 | 0.9682 | 1410 | 1425.2 | 3.3889 | 3.0427 | 6.2438 | 2539.5 | 2718 | 5.5912 | 3.1443 | 7.4365
| 105 | 314.6 | 680.11 | 8.0359e-05 | 6274.9 | 0.5293 | 0.0014703 | 1414000 | 1429400 | 3395.9 | 3042.5 | 826.02 | 0.03272 | 0.011058 |  | 105 | 314.6 | 58.946 | 2.0416e-05 | 7513.3 | 0.081245 | 0.016965 | 2538000 | 2716100 | 5585.1 | 3153.8 | 469.43 | 0.9626 | 1414 | 1429.4 | 3.3959 | 3.0425 | 6.2749 | 2538 | 2716.1 | 5.5851 | 3.1538 | 7.5133
| 106 | 315.31 | 678.45 | 8.0092e-05 | 6306.6 | 0.52811 | 0.0014739 | 1418100 | 1433700 | 3402.8 | 3042.4 | 821.8 | 0.033377 | 0.010901 |  | 106 | 315.31 | 59.655 | 2.0461e-05 | 7591.2 | 0.081846 | 0.016763 | 2536500 | 2714200 | 5578.9 | 3163.2 | 468.8 | 0.95705 | 1418.1 | 1433.7 | 3.4028 | 3.0424 | 6.3066 | 2536.5 | 2714.2 | 5.5789 | 3.1632 | 7.5912
| 107 | 316.01 | 676.79 | 7.9827e-05 | 6338.7 | 0.52692 | 0.0014776 | 1422100 | 1437900 | 3409.7 | 3042.3 | 817.58 | 0.034041 | 0.010746 |  | 107 | 316.01 | 60.37 | 2.0506e-05 | 7670.3 | 0.082453 | 0.016565 | 2535000 | 2712300 | 5572.8 | 3172.6 | 468.18 | 0.95157 | 1422.1 | 1437.9 | 3.4097 | 3.0423 | 6.3387 | 2535 | 2712.3 | 5.5728 | 3.1726 | 7.6703
| 108 | 316.7 | 675.13 | 7.9564e-05 | 6371.4 | 0.52573 | 0.0014812 | 1426100 | 1442100 | 3416.6 | 3042.3 | 813.38 | 0.034713 | 0.010592 |  | 108 | 316.7 | 61.089 | 2.0552e-05 | 7750.7 | 0.083068 | 0.01637 | 2533500 | 2710300 | 5566.7 | 3182 | 467.54 | 0.94614 | 1426.1 | 1442.1 | 3.4166 | 3.0423 | 6.3714 | 2533.5 | 2710.3 | 5.5667 | 3.182 | 7.7507
| 109 | 317.39 | 673.47 | 7.9302e-05 | 6404.6 | 0.52455 | 0.0014848 | 1430100 | 1446300 | 3423.4 | 3042.3 | 809.18 | 0.035393 | 0.010439 |  | 109 | 317.39 | 61.812 | 2.0597e-05 | 7832.4 | 0.08369 | 0.016178 | 2532000 | 2708300 | 5560.6 | 3191.5 | 466.91 | 0.94076 | 1430.1 | 1446.3 | 3.4234 | 3.0423 | 6.4046 | 2532 | 2708.3 | 5.5606 | 3.1915 | 7.8324
| 110 | 318.08 | 671.81 | 7.9042e-05 | 6438.3 | 0.52337 | 0.0014885 | 1434100 | 1450400 | 3430.3 | 3042.4 | 805 | 0.03608 | 0.010287 |  | 110 | 318.08 | 62.541 | 2.0642e-05 | 7915.4 | 0.084321 | 0.01599 | 2530500 | 2706300 | 5554.5 | 3200.9 | 466.27 | 0.93544 | 1434.1 | 1450.4 | 3.4303 | 3.0424 | 6.4383 | 2530.5 | 2706.3 | 5.5545 | 3.2009 | 7.9154
| 111 | 318.76 | 670.15 | 7.8783e-05 | 6472.6 | 0.52219 | 0.0014922 | 1438000 | 1454600 | 3437 | 3042.5 | 800.83 | 0.036776 | 0.010137 |  | 111 | 318.76 | 63.274 | 2.0688e-05 | 7999.8 | 0.084959 | 0.015804 | 2528900 | 2704300 | 5548.4 | 3210.2 | 465.63 | 0.93017 | 1438 | 1454.6 | 3.437 | 3.0425 | 6.4726 | 2528.9 | 2704.3 | 5.5484 | 3.2102 | 7.9998
| 112 | 319.43 | 668.49 | 7.8526e-05 | 6507.5 | 0.52101 | 0.0014959 | 1442000 | 1458700 | 3443.8 | 3042.6 | 796.66 | 0.03748 | 0.0099887 |  | 112 | 319.43 | 64.012 | 2.0734e-05 | 8085.5 | 0.085605 | 0.015622 | 2527300 | 2702300 | 5542.3 | 3219.6 | 464.98 | 0.92495 | 1442 | 1458.7 | 3.4438 | 3.0426 | 6.5075 | 2527.3 | 2702.3 | 5.5423 | 3.2196 | 8.0855
| 113 | 320.11 | 666.83 | 7.827e-05 | 6543 | 0.51984 | 0.0014996 | 1445900 | 1462900 | 3450.5 | 3042.8 | 792.51 | 0.038192 | 0.0098413 |  | 113 | 320.11 | 64.756 | 2.078e-05 | 8172.7 | 0.08626 | 0.015443 | 2525800 | 2700300 | 5536.3 | 3229 | 464.33 | 0.91977 | 1445.9 | 1462.9 | 3.4505 | 3.0428 | 6.543 | 2525.8 | 2700.3 | 5.5363 | 3.229 | 8.1727
| 114 | 320.77 | 665.17 | 7.8016e-05 | 6579 | 0.51866 | 0.0015034 | 1449900 | 1467000 | 3457.2 | 3043 | 788.36 | 0.038912 | 0.0096952 |  | 114 | 320.77 | 65.504 | 2.0826e-05 | 8261.4 | 0.086923 | 0.015266 | 2524200 | 2698200 | 5530.2 | 3238.4 | 463.68 | 0.91465 | 1449.9 | 1467 | 3.4572 | 3.043 | 6.579 | 2524.2 | 2698.2 | 5.5302 | 3.2384 | 8.2614
| 115 | 321.43 | 663.51 | 7.7762e-05 | 6615.7 | 0.51749 | 0.0015071 | 1453800 | 1471100 | 3463.8 | 3043.3 | 784.22 | 0.039641 | 0.0095503 |  | 115 | 321.43 | 66.257 | 2.0873e-05 | 8351.6 | 0.087595 | 0.015093 | 2522600 | 2696100 | 5524.1 | 3247.8 | 463.02 | 0.90957 | 1453.8 | 1471.1 | 3.4638 | 3.0433 | 6.6157 | 2522.6 | 2696.1 | 5.5241 | 3.2478 | 8.3516
| 116 | 322.09 | 661.85 | 7.751e-05 | 6653 | 0.51632 | 0.0015109 | 1457700 | 1475200 | 3470.5 | 3043.6 | 780.09 | 0.040379 | 0.0094067 |  | 116 | 322.09 | 67.016 | 2.092e-05 | 8443.4 | 0.088277 | 0.014922 | 2520900 | 2694000 | 5518.1 | 3257.2 | 462.36 | 0.90454 | 1457.7 | 1475.2 | 3.4705 | 3.0436 | 6.653 | 2520.9 | 2694 | 5.5181 | 3.2572 | 8.4434
| 117 | 322.74 | 660.18 | 7.7259e-05 | 6691 | 0.51516 | 0.0015147 | 1461600 | 1479300 | 3477.1 | 3044 | 775.97 | 0.041126 | 0.0092644 |  | 117 | 322.74 | 67.78 | 2.0967e-05 | 8536.8 | 0.088967 | 0.014754 | 2519300 | 2691900 | 5512 | 3266.6 | 461.69 | 0.89955 | 1461.6 | 1479.3 | 3.4771 | 3.044 | 6.691 | 2519.3 | 2691.9 | 5.512 | 3.2666 | 8.5368
| 118 | 323.39 | 658.52 | 7.701e-05 | 6729.7 | 0.51399 | 0.0015186 | 1465400 | 1483300 | 3483.6 | 3044.4 | 771.86 | 0.041882 | 0.0091233 |  | 118 | 323.39 | 68.55 | 2.1014e-05 | 8631.8 | 0.089668 | 0.014588 | 2517600 | 2689800 | 5506 | 3275.9 | 461.03 | 0.89461 | 1465.4 | 1483.3 | 3.4836 | 3.0444 | 6.7297 | 2517.6 | 2689.8 | 5.506 | 3.2759 | 8.6318
| 119 | 324.04 | 656.85 | 7.6761e-05 | 6769 | 0.51283 | 0.0015224 | 1469300 | 1487400 | 3490.2 | 3044.9 | 767.75 | 0.042647 | 0.0089834 |  | 119 | 324.04 | 69.325 | 2.1062e-05 | 8728.5 | 0.090378 | 0.014425 | 2516000 | 2687600 | 5500 | 3285.3 | 460.36 | 0.8897 | 1469.3 | 1487.4 | 3.4902 | 3.0449 | 6.769 | 2516 | 2687.6 | 5.5 | 3.2853 | 8.7285
| 120 | 324.68 | 655.18 | 7.6513e-05 | 6809.1 | 0.51167 | 0.0015263 | 1473100 | 1491500 | 3496.7 | 3045.4 | 763.65 | 0.043422 | 0.0088447 |  | 120 | 324.68 | 70.106 | 2.1109e-05 | 8827 | 0.091098 | 0.014264 | 2514300 | 2685400 | 5493.9 | 3294.7 | 459.68 | 0.88484 | 1473.1 | 1491.5 | 3.4967 | 3.0454 | 6.8091 | 2514.3 | 2685.4 | 5.4939 | 3.2947 | 8.827
| 121 | 325.31 | 653.51 | 7.6267e-05 | 6849.9 | 0.51051 | 0.0015302 | 1477000 | 1495500 | 3503.2 | 3045.9 | 759.56 | 0.044207 | 0.0087072 |  | 121 | 325.31 | 70.892 | 2.1157e-05 | 8927.3 | 0.091829 | 0.014106 | 2512600 | 2683300 | 5487.9 | 3304.1 | 459 | 0.88002 | 1477 | 1495.5 | 3.5032 | 3.0459 | 6.8499 | 2512.6 | 2683.3 | 5.4879 | 3.3041 | 8.9273
| 122 | 325.94 | 651.84 | 7.6021e-05 | 6891.6 | 0.50935 | 0.0015341 | 1480800 | 1499500 | 3509.7 | 3046.5 | 755.47 | 0.045002 | 0.0085709 |  | 122 | 325.94 | 71.684 | 2.1206e-05 | 9029.5 | 0.09257 | 0.01395 | 2510900 | 2681000 | 5481.9 | 3313.5 | 458.32 | 0.87523 | 1480.8 | 1499.5 | 3.5097 | 3.0465 | 6.8916 | 2510.9 | 2681 | 5.4819 | 3.3135 | 9.0295
| 123 | 326.57 | 650.16 | 7.5777e-05 | 6933.9 | 0.50819 | 0.0015381 | 1484600 | 1503600 | 3516.1 | 3047.2 | 751.39 | 0.045807 | 0.0084358 |  | 123 | 326.57 | 72.483 | 2.1254e-05 | 9133.6 | 0.093323 | 0.013796 | 2509100 | 2678800 | 5475.8 | 3322.9 | 457.63 | 0.87049 | 1484.6 | 1503.6 | 3.5161 | 3.0472 | 6.9339 | 2509.1 | 2678.8 | 5.4758 | 3.3229 | 9.1336
| 124 | 327.19 | 648.49 | 7.5533e-05 | 6977.2 | 0.50704 | 0.0015421 | 1488500 | 1507600 | 3522.6 | 3047.9 | 747.32 | 0.046623 | 0.0083018 |  | 124 | 327.19 | 73.287 | 2.1303e-05 | 9239.6 | 0.094087 | 0.013645 | 2507400 | 2676600 | 5469.8 | 3332.3 | 456.95 | 0.86578 | 1488.5 | 1507.6 | 3.5226 | 3.0479 | 6.9772 | 2507.4 | 2676.6 | 5.4698 | 3.3323 | 9.2396
| 125 | 327.81 | 646.81 | 7.529e-05 | 7021.2 | 0.50588 | 0.0015461 | 1492300 | 1511600 | 3529 | 3048.6 | 743.25 | 0.047449 | 0.008169 |  | 125 | 327.81 | 74.097 | 2.1353e-05 | 9347.8 | 0.094862 | 0.013496 | 2505600 | 2674300 | 5463.8 | 3341.7 | 456.25 | 0.8611 | 1492.3 | 1511.6 | 3.529 | 3.0486 | 7.0212 | 2505.6 | 2674.3 | 5.4638 | 3.3417 | 9.3478
| 126 | 328.43 | 645.13 | 7.5049e-05 | 7066.1 | 0.50473 | 0.0015501 | 1496000 | 1515600 | 3535.4 | 3049.5 | 739.18 | 0.048286 | 0.0080373 |  | 126 | 328.43 | 74.914 | 2.1402e-05 | 9458 | 0.09565 | 0.013349 | 2503800 | 2672000 | 5457.7 | 3351.2 | 455.55 | 0.85646 | 1496 | 1515.6 | 3.5354 | 3.0495 | 7.0661 | 2503.8 | 2672 | 5.4577 | 3.3512 | 9.458
| 127 | 329.04 | 643.44 | 7.4807e-05 | 7112 | 0.50358 | 0.0015541 | 1499800 | 1519600 | 3541.8 | 3050.3 | 735.12 | 0.049135 | 0.0079067 |  | 127 | 329.04 | 75.737 | 2.1452e-05 | 9570.4 | 0.09645 | 0.013204 | 2502000 | 2669700 | 5451.7 | 3360.6 | 454.85 | 0.85186 | 1499.8 | 1519.6 | 3.5418 | 3.0503 | 7.112 | 2502 | 2669.7 | 5.4517 | 3.3606 | 9.5704
| 128 | 329.65 | 641.75 | 7.4567e-05 | 7158.8 | 0.50243 | 0.0015582 | 1503600 | 1523600 | 3548.1 | 3051.2 | 731.07 | 0.049995 | 0.0077773 |  | 128 | 329.65 | 76.566 | 2.1502e-05 | 9685 | 0.097262 | 0.013061 | 2500200 | 2667400 | 5445.7 | 3370 | 454.15 | 0.84729 | 1503.6 | 1523.6 | 3.5481 | 3.0512 | 7.1588 | 2500.2 | 2667.4 | 5.4457 | 3.37 | 9.685
| 129 | 330.25 | 640.06 | 7.4328e-05 | 7206.5 | 0.50128 | 0.0015623 | 1507400 | 1527500 | 3554.5 | 3052.2 | 727.02 | 0.050867 | 0.0076489 |  | 129 | 330.25 | 77.402 | 2.1553e-05 | 9802 | 0.098087 | 0.01292 | 2498400 | 2665000 | 5439.6 | 3379.5 | 453.44 | 0.84274 | 1507.4 | 1527.5 | 3.5545 | 3.0522 | 7.2065 | 2498.4 | 2665 | 5.4396 | 3.3795 | 9.802
| 130 | 330.85 | 638.37 | 7.4089e-05 | 7255.2 | 0.50013 | 0.0015665 | 1511100 | 1531500 | 3560.8 | 3053.2 | 722.97 | 0.051751 | 0.0075216 |  | 130 | 330.85 | 78.245 | 2.1604e-05 | 9921.3 | 0.098926 | 0.01278 | 2496500 | 2662700 | 5433.6 | 3388.9 | 452.73 | 0.83823 | 1511.1 | 1531.5 | 3.5608 | 3.0532 | 7.2552 | 2496.5 | 2662.7 | 5.4336 | 3.3889 | 9.9213
| 131 | 331.45 | 636.67 | 7.385e-05 | 7305 | 0.49899 | 0.0015707 | 1514900 | 1535500 | 3567.1 | 3054.3 | 718.92 | 0.052647 | 0.0073954 |  | 131 | 331.45 | 79.094 | 2.1655e-05 | 10043 | 0.099779 | 0.012643 | 2494700 | 2660300 | 5427.5 | 3398.4 | 452.01 | 0.83376 | 1514.9 | 1535.5 | 3.5671 | 3.0543 | 7.305 | 2494.7 | 2660.3 | 5.4275 | 3.3984 | 10.043
| 132 | 332.04 | 634.97 | 7.3613e-05 | 7355.9 | 0.49784 | 0.0015749 | 1518600 | 1539400 | 3573.4 | 3055.4 | 714.88 | 0.053556 | 0.0072703 |  | 132 | 332.04 | 79.95 | 2.1707e-05 | 10168 | 0.10065 | 0.012508 | 2492800 | 2657900 | 5421.5 | 3407.9 | 451.29 | 0.82931 | 1518.6 | 1539.4 | 3.5734 | 3.0554 | 7.3559 | 2492.8 | 2657.9 | 5.4215 | 3.4079 | 10.168
| 133 | 332.63 | 633.27 | 7.3376e-05 | 7407.8 | 0.4967 | 0.0015791 | 1522400 | 1543400 | 3579.6 | 3056.6 | 710.84 | 0.054477 | 0.0071462 |  | 133 | 332.63 | 80.814 | 2.1759e-05 | 10295 | 0.10153 | 0.012374 | 2490900 | 2655500 | 5415.4 | 3417.4 | 450.56 | 0.82488 | 1522.4 | 1543.4 | 3.5796 | 3.0566 | 7.4078 | 2490.9 | 2655.5 | 5.4154 | 3.4174 | 10.295
| 134 | 333.22 | 631.56 | 7.314e-05 | 7460.9 | 0.49556 | 0.0015834 | 1526100 | 1547300 | 3585.9 | 3057.9 | 706.8 | 0.055412 | 0.0070232 |  | 134 | 333.22 | 81.685 | 2.1811e-05 | 10424 | 0.10242 | 0.012242 | 2489000 | 2653000 | 5409.3 | 3426.9 | 449.83 | 0.82049 | 1526.1 | 1547.3 | 3.5859 | 3.0579 | 7.4609 | 2489 | 2653 | 5.4093 | 3.4269 | 10.424
| 135 | 333.8 | 629.85 | 7.2904e-05 | 7515.3 | 0.49442 | 0.0015877 | 1529900 | 1551300 | 3592.1 | 3059.2 | 702.77 | 0.056361 | 0.0069013 |  | 135 | 333.8 | 82.563 | 2.1864e-05 | 10557 | 0.10333 | 0.012112 | 2487000 | 2650500 | 5403.2 | 3436.5 | 449.1 | 0.81612 | 1529.9 | 1551.3 | 3.5921 | 3.0592 | 7.5153 | 2487 | 2650.5 | 5.4032 | 3.4365 | 10.557
| 136 | 334.38 | 628.13 | 7.2668e-05 | 7570.8 | 0.49328 | 0.001592 | 1533600 | 1555200 | 3598.4 | 3060.6 | 698.73 | 0.057324 | 0.0067803 |  | 136 | 334.38 | 83.448 | 2.1917e-05 | 10692 | 0.10426 | 0.011983 | 2485100 | 2648000 | 5397.2 | 3446 | 448.36 | 0.81178 | 1533.6 | 1555.2 | 3.5984 | 3.0606 | 7.5708 | 2485.1 | 2648 | 5.3972 | 3.446 | 10.692
| 137 | 334.96 | 626.41 | 7.2433e-05 | 7627.7 | 0.49214 | 0.0015964 | 1537300 | 1559200 | 3604.6 | 3062 | 694.69 | 0.058301 | 0.0066604 |  | 137 | 334.96 | 84.342 | 2.1971e-05 | 10831 | 0.1052 | 0.011857 | 2483100 | 2645500 | 5391.1 | 3455.6 | 447.62 | 0.80747 | 1537.3 | 1559.2 | 3.6046 | 3.062 | 7.6277 | 2483.1 | 2645.5 | 5.3911 | 3.4556 | 10.831
| 138 | 335.53 | 624.69 | 7.2199e-05 | 7685.9 | 0.491 | 0.0016008 | 1541000 | 1563100 | 3610.8 | 3063.5 | 690.66 | 0.059293 | 0.0065415 |  | 138 | 335.53 | 85.243 | 2.2025e-05 | 10973 | 0.10616 | 0.011731 | 2481100 | 2643000 | 5385 | 3465.2 | 446.87 | 0.80318 | 1541 | 1563.1 | 3.6108 | 3.0635 | 7.6859 | 2481.1 | 2643 | 5.385 | 3.4652 | 10.973
| 139 | 336.1 | 622.95 | 7.1965e-05 | 7745.5 | 0.48987 | 0.0016053 | 1544700 | 1567000 | 3617 | 3065.1 | 686.62 | 0.060301 | 0.0064237 |  | 139 | 336.1 | 86.152 | 2.208e-05 | 11118 | 0.10714 | 0.011607 | 2479100 | 2640400 | 5378.8 | 3474.8 | 446.12 | 0.79891 | 1544.7 | 1567 | 3.617 | 3.0651 | 7.7455 | 2479.1 | 2640.4 | 5.3788 | 3.4748 | 11.118
| 140 | 336.67 | 621.22 | 7.1731e-05 | 7806.6 | 0.48873 | 0.0016097 | 1548400 | 1571000 | 3623.2 | 3066.7 | 682.58 | 0.061324 | 0.0063068 |  | 140 | 336.67 | 87.069 | 2.2135e-05 | 11266 | 0.10814 | 0.011485 | 2477100 | 2637900 | 5372.7 | 3484.5 | 445.36 | 0.79466 | 1548.4 | 1571 | 3.6232 | 3.0667 | 7.8066 | 2477.1 | 2637.9 | 5.3727 | 3.4845 | 11.266
| 141 | 337.23 | 619.48 | 7.1497e-05 | 7869.2 | 0.4876 | 0.0016143 | 1552100 | 1574900 | 3629.3 | 3068.4 | 678.54 | 0.062363 | 0.0061909 |  | 141 | 337.23 | 87.994 | 2.2191e-05 | 11418 | 0.10915 | 0.011364 | 2475000 | 2635300 | 5366.6 | 3494.2 | 444.6 | 0.79044 | 1552.1 | 1574.9 | 3.6293 | 3.0684 | 7.8692 | 2475 | 2635.3 | 5.3666 | 3.4942 | 11.418
| 142 | 337.79 | 617.73 | 7.1264e-05 | 7933.4 | 0.48646 | 0.0016188 | 1555800 | 1578800 | 3635.5 | 3070.2 | 674.5 | 0.063418 | 0.006076 |  | 142 | 337.79 | 88.928 | 2.2247e-05 | 11573 | 0.11018 | 0.011245 | 2472900 | 2632600 | 5360.4 | 3503.8 | 443.83 | 0.78624 | 1555.8 | 1578.8 | 3.6355 | 3.0702 | 7.9334 | 2472.9 | 2632.6 | 5.3604 | 3.5038 | 11.573
| 143 | 338.35 | 615.98 | 7.1031e-05 | 7999.3 | 0.48533 | 0.0016234 | 1559500 | 1582700 | 3641.7 | 3072.1 | 670.45 | 0.064491 | 0.0059621 |  | 143 | 338.35 | 89.871 | 2.2303e-05 | 11733 | 0.11124 | 0.011127 | 2470900 | 2630000 | 5354.2 | 3513.6 | 443.06 | 0.78206 | 1559.5 | 1582.7 | 3.6417 | 3.0721 | 7.9993 | 2470.9 | 2630 | 5.3542 | 3.5136 | 11.733
| 144 | 338.9 | 614.22 | 7.0798e-05 | 8066.8 | 0.4842 | 0.0016281 | 1563200 | 1586700 | 3647.8 | 3074 | 666.4 | 0.065581 | 0.0058492 |  | 144 | 338.9 | 90.822 | 2.2361e-05 | 11896 | 0.11231 | 0.011011 | 2468700 | 2627300 | 5348.1 | 3523.3 | 442.29 | 0.7779 | 1563.2 | 1586.7 | 3.6478 | 3.074 | 8.0668 | 2468.7 | 2627.3 | 5.3481 | 3.5233 | 11.896
| 145 | 339.45 | 612.45 | 7.0565e-05 | 8136.2 | 0.48307 | 0.0016328 | 1566900 | 1590600 | 3653.9 | 3076 | 662.35 | 0.066689 | 0.0057372 |  | 145 | 339.45 | 91.783 | 2.2418e-05 | 12063 | 0.1134 | 0.010895 | 2466600 | 2624600 | 5341.8 | 3533.1 | 441.51 | 0.77376 | 1566.9 | 1590.6 | 3.6539 | 3.076 | 8.1362 | 2466.6 | 2624.6 | 5.3418 | 3.5331 | 12.063
| 146 | 340 | 610.68 | 7.0333e-05 | 8207.5 | 0.48194 | 0.0016375 | 1570600 | 1594500 | 3660.1 | 3078.1 | 658.29 | 0.067816 | 0.0056262 |  | 146 | 340 | 92.752 | 2.2477e-05 | 12235 | 0.11451 | 0.010781 | 2464500 | 2621900 | 5335.6 | 3542.9 | 440.72 | 0.76964 | 1570.6 | 1594.5 | 3.6601 | 3.0781 | 8.2075 | 2464.5 | 2621.9 | 5.3356 | 3.5429 | 12.235
| 147 | 340.54 | 608.9 | 7.01e-05 | 8280.7 | 0.48081 | 0.0016423 | 1574300 | 1598400 | 3666.2 | 3080.3 | 654.23 | 0.068963 | 0.0055162 |  | 147 | 340.54 | 93.731 | 2.2536e-05 | 12410 | 0.11565 | 0.010669 | 2462300 | 2619100 | 5329.4 | 3552.8 | 439.93 | 0.76554 | 1574.3 | 1598.4 | 3.6662 | 3.0803 | 8.2807 | 2462.3 | 2619.1 | 5.3294 | 3.5528 | 12.41
| 148 | 341.08 | 607.11 | 6.9868e-05 | 8356 | 0.47969 | 0.0016471 | 1578000 | 1602300 | 3672.3 | 3082.5 | 650.16 | 0.070129 | 0.0054071 |  | 148 | 341.08 | 94.72 | 2.2595e-05 | 12591 | 0.11681 | 0.010557 | 2460100 | 2616300 | 5323.1 | 3562.7 | 439.13 | 0.76145 | 1578 | 1602.3 | 3.6723 | 3.0825 | 8.356 | 2460.1 | 2616.3 | 5.3231 | 3.5627 | 12.591
| 149 | 341.62 | 605.32 | 6.9635e-05 | 8433.5 | 0.47856 | 0.001652 | 1581700 | 1606300 | 3678.4 | 3084.9 | 646.08 | 0.071315 | 0.0052989 |  | 149 | 341.62 | 95.718 | 2.2655e-05 | 12776 | 0.11799 | 0.010447 | 2457900 | 2613500 | 5316.9 | 3572.6 | 438.33 | 0.75738 | 1581.7 | 1606.3 | 3.6784 | 3.0849 | 8.4335 | 2457.9 | 2613.5 | 5.3169 | 3.5726 | 12.776
| 150 | 342.16 | 603.52 | 6.9403e-05 | 8513.2 | 0.47744 | 0.001657 | 1585300 | 1610200 | 3684.6 | 3087.3 | 642 | 0.072523 | 0.0051917 |  | 150 | 342.16 | 96.727 | 2.2716e-05 | 12967 | 0.11919 | 0.010338 | 2455600 | 2610700 | 5310.6 | 3582.6 | 437.53 | 0.75333 | 1585.3 | 1610.2 | 3.6846 | 3.0873 | 8.5132 | 2455.6 | 2610.7 | 5.3106 | 3.5826 | 12.967
100 % liquid | 120 | 324.68 | 655.18 | 7.6513e-05 | 6809.1 | 0.51167 | 0.0015263 | 1473100 | 1491500 | 3496.7 | 3045.4 | 763.65 | 0.043422 | 0.0088447 | 100 % vapor | 120 | 324.68 | 70.106 | 2.1109e-05 | 8827 | 0.091098 | 0.014264 | 2514300 | 2685400 | 5493.9 | 3294.7 | 459.68 | 0.88484 | 1473.1 | 1491.5 | 3.4967 | 3.0454 | 6.8091 | 2514.3 | 2685.4 | 5.4939 | 3.2947 | 8.827
100% | 120 | 324.68 | 655.18 | 7.6513e-05 | 6809.1 | 0.51167 | 0.0015263 | 1473100 | 1491500 | 3496.7 | 3045.4 | 763.65 | 0.043422 | 0.0088447 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1473.1 | 1491.5 | 3.4967 | 3.0454 | 6.8091 | 0 | 0 | 0 | 0 | 0
TRUE | 120 | 324.68 | 655.18 | 7.6513e-05 | 6809.1 | 0.51167 | 0.0015263 | 1473100 | 1491500 | 3496.7 | 3045.4 | 763.65 | 0.043422 | [15 empty] | 1473.1 | 1491.5 | 3.4967 | 3.0454 | 6.8091
https://webbook,nist,gov/cgi/fluid,cgi?PLow=60&PHigh=120&PInc=1&Digits=5&ID=C7732185&Action=Load&Type=SatT&TUnit=C&PUnit=bar&DUnit=kg%2Fm3&HUnit=kJ%2Fkg&WUnit=m%2Fs&VisUnit=Pa*s&STUnit=N%2Fm&RefState=DEF

## k-T
Deposit type | Thermal conductivity | Temperature | Carbon steel (4L7) | Austenitic stainless steel (304L) | Sanicro 38 | Magnetite (Fe3O4) | Hematite (Fe2O3) | Temperature | Magnetite (Fe3O4) | Deposits | Smelt
| (W/mK) |  | Thermal conductivity | [5 empty] | Thermal conductivity
|  | (oC) | (W/mK) |  |  |  |  | (oC) | (W/mK)
Iron oxides (3,0 W/mK) | 3 | 20 |  | 15 |  |  |  | 0 | 3 | 0.3 | 0.6
Iron and other impurities (0,3 W/mK) | 0.3 | 23 |  |  | 11 |  |  | 700 | 3 | 0.3 | 0.6
|  | 100 | 48 | 16 | 12 | 3.72 | 5.92
Iron and other impurities (0,3 W/mK) | 0.3 | 200 | 47 | 18 |  | 3.58 | 2.25
|  | 300 | 46 | 20 | 16 | 3.44 | 4.59
|  | 400 | 44 | 22 |  | 3.31 | 3.93
|  | 500 | 42 | 23 | 19
|  | 600 |  | 25
|  | 700 |  | 26
|  | Source | Sanicro® 67 for black liquor recovery boilers — Alleima | Alleima® 3R12 — Alleima | Sanicro® 67 for black liquor recovery boilers — Alleima | (Molgaard and Smeltzer, 1971)
Equation parameter k carbon steel a | acs | -2.1429e-05
Equation parameter k carbon steel b | bcs | -0.0021429
Equation parameter k carbon steel c | ccs | 48.4
Equation parameter k cladding 304 a | a304 | 0.016827
Equation parameter k cladding 304 b | b304 | 14.6936
Equation parameter k cladding 38 a | a38 | 0.017227
Equation parameter k cladding 38 b | b38 | 10.5249

## CR-T
Source | 304 temperature | 304 CR | Sanicro 38 temperature | Sanicro 38 CR |  |  | AISI 304 | Sanicro 38
| (oC) | (mm/y) | (oC) | (mm/y) | Equation parameter CR a | aCR | -9.7292e-06 | 1.3254e-05
(Kiwa, 2014) |  |  | 374.6501 | 0 | Equation parameter CR b | bCR | 0.017162 | -0.0097262
(Khodahami, 2024) | 381.059 | 0.05928 |  |  | Equation parameter CR c | cCR | -5.0678 | 1.7836
(Pohjanne, 2013) | 440 | 0.6 | 440 | 0.07
Chosen point |  |  | 490 | 0.2 | Temperature 0 CR | TnCR | 375.0137 | 374.6512
(Liikola, 2015) | 655.1434 | 2
[9 empty] | Temperature [oC] | Corrosion rating [mm/y] |  |  | H2S concentration ppm | Comments | Source
[10 empty] | Carbon steel | Austenitic stainless steel | Sanicro 38
[9 empty] | 250 | 0.1 | 0 | 0 | 1000 | AISI 304, AISI 310 | (Tavares & Karjunen, 2020)
[9 empty] | 300 | 0.4 | 0.1 | 0 | 1000
[9 empty] | 350 | 0.8 | 0.3 | 0 | 1000
[9 empty] | 400 | 1.7 | 0.6 | 0 | 1000
[9 empty] | 450 | 3.3 | 1.4 | 0.2 | 1000
[9 empty] | 500 | 5.7 | 2.1 | 0.3 | 1000
[9 empty] | 250 | 0.1 | 0 |  | 10000 | AISI 304 | (Salmenoja and Tuiremo, 2001 from Vakkilainen, 2005)
[9 empty] | 300 | 0.2 | 0 |  | 10000
[9 empty] | 350 | 0.4 | 0 |  | 10000
[9 empty] | 400 | 0.7 | 0.1 |  | 10000
[9 empty] | 450 | 1.3 | 0.3 |  | 10000
[9 empty] | 500 | 2.3 | 0.5 |  | 10000
[9 empty] | 550 | 3.5 | 0.8 |  | 10000
[9 empty] | 600 | 4.7 | 1.3 |  | 10000
[9 empty] | 360 |  | 0.02 | 0.02 | 5000 (H2S-N2 vppm) | 304L | (Mäkipää et al., 2001)
[9 empty] | 400 |  | 0.05 | 0.15 | 5000 (H2S-N2 vppm)
[9 empty] | 300 | 0.8 | 0 |  | 10000 | 5 % Cr carbon steel, 18Cr-8Ni | (Nickel, n.d.)
[9 empty] | 350 | 1.9 | 0 |  | 10000
[9 empty] | 400 |  | 0 |  | 10000
[9 empty] | 450 |  | 0.1 |  | 10000
[9 empty] | 420 |  | 0.12 |  | Low | S30403 | (Nimmervoll et al., 2022)
[9 empty] | 480 |  | 0.23 |  | Low
[9 empty] | 580 |  | 0.8 |  | Low
[9 empty] | 420 |  | 0.12 |  | Medium
[9 empty] | 480 |  | 0.27 |  | Medium
[9 empty] | 580 |  | 0.95 |  | Medium
[9 empty] | 420 |  | 0.16 |  | High
[9 empty] | 480 |  | 0.28 |  | High
[9 empty] | 580 |  | 1.32 |  | High
[9 empty] | 440 |  | 0.050633 | 0.098765 | 500 | 304L (no water vapor) | (Yli-Olli et al., 2007)
[9 empty] | 440 |  | 0.075949 | 0.14815 | 1000
[9 empty] | 440 |  | 0.063291 | 0.12963 | 2500
[9 empty] | 440 |  | 0.088608 | 0.2037 | 5000
[9 empty] | 440 | 4 | 0.6 | 0.07 |  | 304L | (Pohjanne, 2013)
[9 empty] | High |  | 0.057 | 0 |  | AISI 304 and Sanicro 38 | (Kiwa, 2014)
[9 empty] | Varies |  | 0.058 |  |  | AISI 304 | (Khodahami, 2024)
0.059
0.041
0.047
0.03
0.026
[9 empty] | High |  | 2 |  |  | AISI 304 | (Liikola, 2015)

## l-q
Furnace height | Heat flux multiplier | Location | Height % | Heat flux % | Old height | Old heat flux multiplier | New height | New heat flux multiplier | Location | Height | Height | Measured | Calculated
0% | 160% |  |  |  | 0% | 40% | 0% | 68.62% |  | (m) | (%) | (mm/y)
1% | 160% | Primary air ports | 0% | 160% | 10% | 130% | 6.822% | 130% | Pos 1 | 0.75 | 1.98% | 0.058 | 0.059
2% | 160% | Bottom secondary air ports | 5.06% | 159% | 20% | 160% | 16.83% | 160% | Pos 2 | 1.4 | 3.69% | 0.059 | 0.058
3% | 160% | Top secondary air ports | 8.99% | 157% | 30% | 150% | 26.83% | 150% | Pos 3 | 2 | 5.28% | 0.041 | 0.055
4% | 159.5% | Black liquor guns | 22.09% | 144.1% | 40% | 130% | 36.83% | 130% | Pos 4 | 2.6 | 6.86% | 0.047 | 0.053
5% | 159% | Tertiary air port | 32.4% | 131.4% | 50% | 110% | 46.83% | 110% | Pos 5 | 4.6 | 12.14% | 0.03 | 0.039
6% | 158.5% | Nose arch upper edge | 100% | 40% | 60% | 90% | 56.84% | 90% | Pos 6 | 7.1 | 18.73% | 0.026 | 0.016
7% | 158% |  |  |  | 70% | 77% | 66.84% | 75%
8% | 157.5% | 0 | No Match | Out of Range | 80% | 60% | 76.84% | 60%
9% | 157% |  |  |  | 90% | 50% | 86.85% | 50%
10% | 156% | Relative location percentage input | l%i | 4.987% | 100% | 40% | 100% | 40%
11% | 155% | Heat flux multiplier input location | ki | 159%
12% | 154% | Heat flux multiplier input maximum | km | 160% | Height primary old |  | 3.18%
13% | 153% |  |  |  | height primary new |  | 0%
14% | 152%
15% | 151%
16% | 150%
17% | 149%
18% | 148%
19% | 147%
20% | 146.2%
21% | 145.2%
22% | 144.2%
23% | 143.2%
24% | 142.2%
25% | 141.2%
26% | 140.2%
27% | 139.2%
28% | 138.7%
29% | 137%
30% | 135.7%
31% | 133.9%
32% | 132.1%
33% | 130.3%
34% | 128.5%
35% | 127.2%
36% | 125.8%
37% | 124%
38% | 122.2%
39% | 120.4%
40% | 118.6%
41% | 116.7%
42% | 114.9%
43% | 113.1%
44% | 111.3%
45% | 109.5%
46% | 107.6%
47% | 105.8%
48% | 104%
49% | 102.2%
50% | 100.2%
51% | 98.17%
52% | 96.18%
53% | 94.18%
54% | 92.18%
55% | 90.18%
56% | 88.18%
57% | 86.18%
58% | 84.18%
59% | 82.18%
60% | 80.82%
61% | 79.45%
62% | 78.09%
63% | 76.73%
64% | 75.36%
65% | 74%
66% | 72.63%
67% | 71.27%
68% | 69.91%
69% | 68.54%
70% | 67.18%
71% | 65.68%
72% | 64.18%
73% | 62.68%
74% | 61.18%
75% | 59.68%
76% | 58.18%
77% | 56.68%
78% | 55.18%
79% | 53.68%
80% | 52.18%
81% | 51.27%
82% | 50.36%
83% | 49.45%
84% | 48.54%
85% | 47.63%
86% | 46.73%
87% | 45.82%
88% | 44.91%
89% | 44%
90% | 43.09%
91% | 42.18%
92% | 41.07%
93% | 40.96%
94% | 40.85%
95% | 40.74%
96% | 40.62%
97% | 40.51%
98% | 40.4%
99% | 40.29%
100% | 40%
Average | 100%

## T-xd, CR-xd
Multiplier | Deposit thickness | Deposit thickness | Tcf 304 | Tcf Sanicro 38 | Tcf 304 max | Tcf Sanicro 38 max | 304 CR | Sanicro 38 CR | 304 CR max | Sanicro 38 CR max | Term | Symbol | Unit | AISI 304 | Sanicro 38 | AISI 304 max | Sanicro 38 max
| (m) | (μm) | (oC) | (oC) | (oC) | (oC) | (mm/y) | (mm/y) | (mm/y) | (mm/y) | Average deposit thickness true | xdt | (m) | 0.0001
0 | 0 | 0 | 369.2511 | 372.1904 | 369.5274 | 372.4821 | 0 | 0 | 0 | 0 | Heat flux efficiency | qf | (W/m2) | 106823.7664
0.25 | 2.5e-05 | 25 | 383.4058 | 386.3452 | 383.7706 | 386.7253 | 0.082102 | 0.0042102 | 0.08564 | 0.0044079 | Heat flux true | qt | (W/m2) | 169856.8349 |  | 170918.0262
0.5 | 5e-05 | 50 | 397.5605 | 400.4999 | 398.0138 | 400.9685 | 0.21748 | 0.014156 | 0.22175 | 0.014576 | Cladding thickness true | xclt | (m) | 0.00165 | 0.00165 | 0.00165 | 0.00165
0.75 | 7.5e-05 | 75 | 411.7153 | 414.6546 | 412.2569 | 415.2116 | 0.34896 | 0.029412 | 0.35391 | 0.030121 | Thermal conductivity cladding true | kclt | (W/mK) | 21.6417 | 17.6382 | 21.651 | 17.6478
1 | 0.0001 | 100 | 425.87 | 428.8094 | 426.5001 | 429.4548 | 0.47653 | 0.04998 | 0.48212 | 0.051044 | Carbon steel thickness true | xcst | (m) | 0.00488 | 0.00488 | 0.00488 | 0.00488
1.25 | 0.000125 | 125 | 440.0247 | 442.9641 | 440.7433 | 443.698 | 0.60021 | 0.075859 | 0.60639 | 0.077345 | Thermal conductivity carbon steel true | kcst | (W/mK) | 44.2259 |  | 44.2176
1.5 | 0.00015 | 150 | 454.1795 | 457.1189 | 454.9864 | 457.9411 | 0.71999 | 0.10705 | 0.72671 | 0.10902 | Average deposit thickness true | xdt | (m) | 0.0001
1.75 | 0.000175 | 175 | 468.3342 | 471.2736 | 469.2296 | 472.1843 | 0.83588 | 0.14355 | 0.84308 | 0.14608 | Thermal conductivity deposits true | kdt | (W/mK) | 0.3
2 | 0.0002 | 200 | 482.489 | 485.4283 | 483.4728 | 486.4275 | 0.94786 | 0.18536 | 0.9555 | 0.18851 | Temperature deposit surface facing water | Twd | (oC) | 337.5584 |  | 337.6389
[11 empty] | Heat transfer coefficient | h | (W/m2K) | 13189.28
[11 empty] | Temperature water/steam | Tw | (oC) | 324.68
[11 empty] | Equation parameter CR a | aCR |  | -9.7292e-06 | 1.3254e-05 | -9.7292e-06 | 1.3254e-05
[11 empty] | Equation parameter CR b | bCR |  | 0.017162 | -0.0097262 | 0.017162 | -0.0097262
[11 empty] | Equation parameter CR c | cCR |  | -5.0678 | 1.7836 | -5.0678 | 1.7836
[11 empty] | Temperature 0 CR | TnCR | (oC) | 375.0137 | 374.6512 | 375.0137 | 374.6512

## l-CR
Furnace height | Heat flux multiplier | Heat flux location | Tcf 304 | Tcf Sanicro 38 | 304 CR | Sanicro 38 CR | Term | Symbol | Unit | AISI 304 | Sanicro 38
(%) | (%) | (W/m2) | (oC) | (oC) | (mm/y) | (mm/y) | Heat flux efficiency | qf | (W/m2) | 106823.7664
0% | 160% | 170918.0262 | 426.5022 | 429.4599 | 0.48214 | 0.051053 | Cladding thickness true | xclt | (m) | 0.00165 | 0.00165
1% | 160% | 170918.0262 | 426.5022 | 429.4599 | 0.48214 | 0.051053 | Thermal conductivity cladding true | kclt | (W/mK) | 21.6417 | 17.6382
2% | 160% | 170918.0262 | 426.5022 | 429.4599 | 0.48214 | 0.051053 | Carbon steel thickness true | xcst | (m) | 0.00488 | 0.00488
3% | 160% | 170918.0262 | 426.5022 | 429.4599 | 0.48214 | 0.051053 | Thermal conductivity carbon steel true | kcst | (W/mK) | 44.2259
4% | 159.5% | 170383.9073 | 426.184 | 429.1325 | 0.47932 | 0.050511 | Average deposit thickness true | xdt | (m) | 0.0001
5% | 159% | 169849.7885 | 425.8658 | 428.8051 | 0.4765 | 0.049973 | Thermal conductivity deposits true | kdt | (W/mK) | 0.3
6% | 158.5% | 169315.6697 | 425.5476 | 428.4776 | 0.47367 | 0.049437 | Heat transfer coefficient | h | (W/m2K) | 13189.28
7% | 158% | 168781.5508 | 425.2294 | 428.1502 | 0.47084 | 0.048904 | Temperature water/steam | Tw | (oC) | 324.68
8% | 157.5% | 168247.432 | 424.9112 | 427.8228 | 0.46802 | 0.048374 | Equation parameter CR a | aCR |  | -9.7292e-06 | 1.3254e-05
9% | 157% | 167713.3132 | 424.593 | 427.4953 | 0.46518 | 0.047847 | Equation parameter CR b | bCR |  | 0.017162 | -0.0097262
10% | 156% | 166645.0755 | 423.9566 | 426.8404 | 0.45952 | 0.046801 | Equation parameter CR c | cCR |  | -5.0678 | 1.7836
11% | 155% | 165576.8379 | 423.3203 | 426.1856 | 0.45384 | 0.045766 | Temperature 0 CR | TnCR | (oC) | 375.0137 | 374.6512
12% | 154% | 164508.6002 | 422.6839 | 425.5307 | 0.44816 | 0.044743
13% | 153% | 163440.3625 | 422.0475 | 424.8758 | 0.44247 | 0.043731
14% | 152% | 162372.1249 | 421.4111 | 424.2209 | 0.43677 | 0.042731
15% | 151% | 161303.8872 | 420.7747 | 423.5661 | 0.43106 | 0.041742
16% | 150% | 160235.6495 | 420.1383 | 422.9112 | 0.42534 | 0.040764
17% | 149% | 159167.4119 | 419.5019 | 422.2563 | 0.41962 | 0.039798
18% | 148% | 158099.1742 | 418.8655 | 421.6014 | 0.41389 | 0.038843
19% | 147% | 157030.9365 | 418.2291 | 420.9466 | 0.40815 | 0.037899
20% | 146.2% | 156165.664 | 417.7137 | 420.4161 | 0.4035 | 0.037143
21% | 145.2% | 155097.4264 | 417.0773 | 419.7612 | 0.39774 | 0.03622
22% | 144.2% | 154029.1887 | 416.4409 | 419.1064 | 0.39198 | 0.035308
23% | 143.2% | 152960.951 | 415.8045 | 418.4515 | 0.38621 | 0.034408
24% | 142.2% | 151892.7134 | 415.1681 | 417.7966 | 0.38044 | 0.033519
25% | 141.2% | 150824.4757 | 414.5317 | 417.1417 | 0.37465 | 0.032642
26% | 140.2% | 149756.2381 | 413.8953 | 416.4869 | 0.36886 | 0.031775
27% | 139.2% | 148688.0004 | 413.2589 | 415.832 | 0.36306 | 0.030921
28% | 138.7% | 148153.8816 | 412.9408 | 415.5046 | 0.36015 | 0.030497
29% | 137% | 146337.8775 | 411.8589 | 414.3913 | 0.35027 | 0.02908
30% | 135.7% | 144997.7248 | 411.0605 | 413.5697 | 0.34296 | 0.028055
31% | 133.9% | 143055.4745 | 409.9034 | 412.379 | 0.33234 | 0.026601
32% | 132.1% | 141113.2242 | 408.7464 | 411.1883 | 0.3217 | 0.025185
33% | 130.3% | 139170.9739 | 407.5893 | 409.9977 | 0.31103 | 0.023807
34% | 128.5% | 137228.7236 | 406.4322 | 408.807 | 0.30034 | 0.022466
35% | 127.2% | 135869.1484 | 405.6223 | 407.9735 | 0.29284 | 0.021549
36% | 125.8% | 134412.4607 | 404.7545 | 407.0805 | 0.28479 | 0.020588
37% | 124% | 132470.2104 | 403.5974 | 405.8898 | 0.27403 | 0.019339
38% | 122.2% | 130527.9601 | 402.4403 | 404.6991 | 0.26324 | 0.018128
39% | 120.4% | 128585.7098 | 401.2833 | 403.5084 | 0.25243 | 0.016954
40% | 118.6% | 126643.4595 | 400.1262 | 402.3178 | 0.2416 | 0.015818
41% | 116.7% | 124701.2092 | 398.9691 | 401.1271 | 0.23074 | 0.014719
42% | 114.9% | 122758.9589 | 397.8121 | 399.9364 | 0.21985 | 0.013658
43% | 113.1% | 120816.7086 | 396.655 | 398.7457 | 0.20893 | 0.012635
44% | 111.3% | 118874.4583 | 395.4979 | 397.555 | 0.19799 | 0.011649
45% | 109.5% | 116932.208 | 394.3408 | 396.3644 | 0.18703 | 0.010701
46% | 107.6% | 114989.9577 | 393.1838 | 395.1737 | 0.17604 | 0.0097901
47% | 105.8% | 113047.7074 | 392.0267 | 393.983 | 0.16502 | 0.008917
48% | 104% | 111105.4571 | 390.8696 | 392.7923 | 0.15397 | 0.0080815
49% | 102.2% | 109163.2068 | 389.7126 | 391.6016 | 0.1429 | 0.0072836
50% | 100.2% | 107026.7315 | 388.4398 | 390.2919 | 0.13069 | 0.0064493
51% | 98.17% | 104868.8914 | 387.1543 | 388.969 | 0.11833 | 0.0056528
52% | 96.18% | 102743.0985 | 385.8879 | 387.6658 | 0.10612 | 0.0049135
53% | 94.18% | 100606.6232 | 384.6151 | 386.3561 | 0.09382 | 0.0042158
54% | 92.18% | 98470.1478 | 383.3423 | 385.0463 | 0.081486 | 0.0035636
55% | 90.18% | 96333.6725 | 382.0695 | 383.7366 | 0.069121 | 0.0029569
56% | 88.18% | 94197.1972 | 380.7968 | 382.4268 | 0.056724 | 0.0023957
57% | 86.18% | 92060.7218 | 379.524 | 381.1171 | 0.044296 | 0.0018799
58% | 84.18% | 89924.2465 | 378.2512 | 379.8073 | 0.031836 | 0.0014096
59% | 82.18% | 87787.7712 | 376.9784 | 378.4976 | 0.019344 | 0.00098475
60% | 80.82% | 86331.0835 | 376.1106 | 377.6046 | 0.010809 | 0.00072116
61% | 79.45% | 84874.3957 | 375.2428 | 376.7116 | 0.0022593 | 0.00047872
62% | 78.09% | 83417.708 | 374.375 | 375.8186 | 0 | 0.00025741
63% | 76.73% | 81961.0203 | 373.5072 | 374.9256 | 0 | 5.7245e-05
64% | 75.36% | 80504.3326 | 372.6394 | 374.0325 | 0 | 0
65% | 74% | 79047.6449 | 371.7716 | 373.1395 | 0 | 0
66% | 72.63% | 77590.9571 | 370.9038 | 372.2465 | 0 | 0
67% | 71.27% | 76134.2694 | 370.036 | 371.3535 | 0 | 0
68% | 69.91% | 74677.5817 | 369.1682 | 370.4605 | 0 | 0
69% | 68.54% | 73220.894 | 368.3004 | 369.5675 | 0 | 0
70% | 67.18% | 71764.2062 | 367.4326 | 368.6745 | 0 | 0
71% | 65.68% | 70161.8497 | 366.478 | 367.6922 | 0 | 0
72% | 64.18% | 68559.4932 | 365.5234 | 366.7099 | 0 | 0
73% | 62.68% | 66957.1368 | 364.5688 | 365.7275 | 0 | 0
74% | 61.18% | 65354.7803 | 363.6143 | 364.7452 | 0 | 0
75% | 59.68% | 63752.4238 | 362.6597 | 363.7629 | 0 | 0
76% | 58.18% | 62150.0673 | 361.7051 | 362.7806 | 0 | 0
77% | 56.68% | 60547.7108 | 360.7505 | 361.7983 | 0 | 0
78% | 55.18% | 58945.3543 | 359.7959 | 360.816 | 0 | 0
79% | 53.68% | 57342.9978 | 358.8413 | 359.8337 | 0 | 0
80% | 52.18% | 55740.6413 | 357.8868 | 358.8514 | 0 | 0
81% | 51.27% | 54769.5161 | 357.3082 | 358.256 | 0 | 0
82% | 50.36% | 53798.391 | 356.7297 | 357.6607 | 0 | 0
83% | 49.45% | 52827.2658 | 356.1512 | 357.0653 | 0 | 0
84% | 48.54% | 51856.1407 | 355.5726 | 356.47 | 0 | 0
85% | 47.63% | 50885.0155 | 354.9941 | 355.8747 | 0 | 0
86% | 46.73% | 49913.8904 | 354.4156 | 355.2793 | 0 | 0
87% | 45.82% | 48942.7652 | 353.837 | 354.684 | 0 | 0
88% | 44.91% | 47971.6401 | 353.2585 | 354.0886 | 0 | 0
89% | 44% | 47000.5149 | 352.6799 | 353.4933 | 0 | 0
90% | 43.09% | 46029.3898 | 352.1014 | 352.898 | 0 | 0
91% | 42.18% | 45058.2646 | 351.5229 | 352.3026 | 0 | 0
92% | 41.07% | 43871.3339 | 350.8158 | 351.575 | 0 | 0
93% | 40.96% | 43752.6408 | 350.7451 | 351.5022 | 0 | 0
94% | 40.85% | 43633.9478 | 350.6744 | 351.4294 | 0 | 0
95% | 40.74% | 43515.2547 | 350.6036 | 351.3567 | 0 | 0
96% | 40.62% | 43396.5616 | 350.5329 | 351.2839 | 0 | 0
97% | 40.51% | 43277.8685 | 350.4622 | 351.2112 | 0 | 0
98% | 40.4% | 43159.1755 | 350.3915 | 351.1384 | 0 | 0
99% | 40.29% | 43040.4824 | 350.3208 | 351.0656 | 0 | 0
100% | 40% | 42729.5065 | 350.1355 | 350.875 | 0 | 0

## T-x
Term | Symbol | Unit | AISI 304 | Sanicro 38
Temperature water/steam | Tw | (oC) | 324.68 | 324.68
Temperature deposit surface facing water | Twd | (oC) | 337.5584 | 337.5584
Temperature deposit-carbon steel interface | Tdc | (oC) | 394.1773 | 394.1773
Temperature carbon steel-cladding interface | Tcc | (oC) | 412.9198 | 412.9198
Temperature cladding surface facing furnace | Tcf | (oC) | 425.87 | 428.8094
Temperature smelt surface facing furnace standard | Tss | (oC) | 720 | 720
Water | x_w | (mm) | -1 | -1
Deposit surface facing water | x_wd | (mm) | 0 | 0
Deposit-carbon steel interface | x_dc | (mm) | 0.11 | 0.11
Carbon-steel cladding interface | x_cc | (mm) | 5.66 | 5.66
Cladding surface facing furnace | x_cf | (mm) | 7.48 | 7.48
Smalt surface facing furnace | x_ss | (mm) | 9 | 9
Deposit surface facing water
Water
Deposit-carbon steel interface